All DalMax Sump and Grates (SOFA’S) are Certified under

APSP-16 2017 (PA 2021) and NSF/ANSI/CAN 50-2020

SOFA – Suction Outlet Fitting Assembly

DalMax SOFA’s listed below are IAPMO certified for all custom piping configurations

All suction pipe locations are >16” below top of grate; total flow cannot exceed certified flow rates

| Model Number | Size (inches) | Depth (inches) | Max Port Size (inches) |  | Open Area (inches2) | Certified Max Flow (GPM) |  | Velocity at Max Flow (ft/s) |  | Flow Rate (GPM) At Velocity (ft/s) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Side Port | Bottom Port |  | Floor | Wall | Floor | Wall | 0.5 | 1.0 | 1.5 |

| DalMax-SG-242430 | 24x24 | 30 | 12 | 24 | 357 | 1734 | 1600 | 1.56 | 1.44 | 556 | 1113 | 1669 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DalMax-SG-183625 | 18x36 | 25 | 8 | 24 | 401 | 1984 | 1440 | 1.59 | 1.15 | 625 | 1250 | 1875 |
| DalMax-SG-183628 | 18x36 | 28 | 10 | 24 | 401 | 2480 | 1909 | 1.98 | 1.53 | 625 | 1250 | 1875 |
| DalMax-SG-183634 | 18x36 | 34 | 16 | 24 | 401 | 2869 | 2080 | 2.30 | 1.66 | 625 | 1250 | 1875 |
| DalMax-SG-185427 | 18x54 | 27 | 10 | 24 | 602 | 2872 | 2872 | 1.53 | 1.53 | 938 | 1876 | 2815 |
| DalMax-SG-185429 | 18x54 | 29 | 12 | 24 | 602 | 2944 | 2872 | 1.57 | 1.53 | 938 | 1876 | 2815 |
| DalMax-SG-185434 | 18x54 | 34 | 16 | 24 | 602 | 4412 | N/A | 2.35 | N/A | 938 | 1876 | 2815 |
| DalMax-SG-187234* | 18x72 | 34 | 16 | 24 | 803 | 7715 | N/A | 3.08 | N/A | 1252 | 2504 | 3756 |
| DalMax-SG-187242* | 18x72 | 42 | 24 | 24 | 803 | 7715 | N/A | 3.08 | N/A | 1252 | 2504 | 3756 |
| DalMax-SG-244834* | 24x48 | 34 | 16 | 24 | 714 | 6456 | N/A | 2.90 | N/A | 1113 | 2226 | 3339 |
| DalMax-SG-244842* | 24x48 | 42 | 24 | 24 | 714 | 6456 | N/A | 2.90 | N/A | 113 | 2226 | 3339 |

*Tested flow rate was hydraulically limited due to lab pipe/pump system not sufficient for large size SOFA’s.

*The Lesser of the Q Formula per Section 3.9 of ANSI/APSP/ICC-16-2017 and the velocities derived from the testing of the next size down was considered the most conservative flow rate, based on engineering evaluation.

DalMAX SOFA’s listed below are IAPMO certified for single piping configuration only

| Model Number | Size (inches) | Depth (inches) | Max Port Size (inches) |  | Open Area (inches2) | Certified Max Flow (GPM) |  | Velocity at Max Flow (ft/s) |  | Flow Rate (GPM) at Velocity (ft/s) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Side Port | Bottom Port |  | Floor | Wall | Floor | Wall | 0.5 | 1.0 | 1.5 |

| DalMAX-SG-242412-06 | 24x24 | 12 | 6 | 6 | 357 | 1644 | N/A | 1.50 | N/A | 556 | 1113 | 1669 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DalMAX-SG-242412-04 | 24x24 | 12 | 4 | 4 | 357 | 715 | N/A | 0.64 | N/A | 556 | N/A | N/A |
| DalMAX-SG-242421-BEAST | 24X24 | 21 | 10 | N/A | 357 | 1734 | 1552 | 1.56 | 1.44 | 556 | 1113 | 1669 |

Grate Service Life: 25 Years

Sump Service Life: Life of the Aquatic Facility

REV 2-10-25